## Sheet2
S. No. | PARAMETERS | UoM | DESIGN | UoM | Values (D) | UoM | OPERATING | UoM | VALUES (O)
1 | LOAD | MW | 300 | MW | 300 | MW | 299.5 | MW | 299.5
2 | AMBIENT PRESSURE | bar (a) | 1.013 | bar (a) | 1.013 | bar | 1.013 | bar (a) | 1.013
3 | AMBIENT TEMPERATURE | °C | 27.5 | °C | 27.5 | °C | 27.5 | °C | 27.5
4 | RELATIVE HUMIDITY | % | 60 | % | 60 | % | 60 | % | 60
MS
5 | 1ST STAGE PRESS | MPa (a) | 11.94 | bar (a) | 119.4 | MPa (g) | 11.94 | bar (a) | 120.413
6 | MS FLOW | TPH | 913.624 | kg/h | 913624 | TPH | 906.2 | kg/h | 906200
7 | MS PRESSURE AT TURBINE I/L | MPa (a) | 16.67 | bar (a) | 166.7 | MPa (g) | 16.67 | bar (a) | 167.713
8 | MS PRESSURE AT BOILER O/L | MPa (a) | 16.89 | bar (a) | 168.9 | MPa (g) | 16.89 | bar (a) | 169.913
9 | MS TEMP AT TV1 | °C | 538 | °C | 538 | °C | 538 | °C | 538
10 | MS TEMP AT TV2 | °C | 538 | °C | 538 | °C | 538 | °C | 538
CRH
11 | HP EXH PRESS | MPa (a) | 3.522 | bar (a) | 35.22 | MPa (g) | 3.43 | bar (a) | 35.313
12 | CRH PRESSURE | MPa (a) | 3.522 | bar (a) | 35.22 | MPa (g) | 3.34 | bar (a) | 34.413
13 | CRH TEMP | °C | 315.8 | °C | 315.8 | °C | 317.17 | °C | 317.17
14 | AFTER HPBP PRESS | MPa (a) | 3.31 | bar (a) | 33.1 | MPa (g) | 3.31 | bar (a) | 34.113
15 | AFTER HPBP TEMP | °C | 344.18 | °C | 344.18 | °C | 344.18 | °C | 344.18
HRH
16 | HRH PRESSURE | MPa (a) | 3.17 | bar (a) | 31.7 | MPa (g) | 2.9 | bar (a) | 30.013
17 | HRH TEMP | °C | 538 | °C | 538 | °C | 540.64 | °C | 540.64
18 | IP I/L LH TEMP | °C | 538 | °C | 538 | °C | 540.36 | °C | 540.36
19 | IP I/L RH TEMP | °C | 538 | °C | 538 | °C | 539.84 | °C | 539.84
20 | FEED WATER FLOW | TPH | 913.624 | kg/h | 913.624 | TPH | 966.75 | kg/h | 966.75
21 | CONDENSOR VACUUM (DCS) |  | -91.25 | bar (a) | 0.1005 |  | -89.18 | bar (a) | 0.1212
22 | CONDENSATE FLOW | TPH | 702.823 | kg/h | 702823 | TPH | 731.92 | kg/h | 731920
DESUPERHEATING
23 | RH LHS DESUP FLOW | TPH | 0 | kg/h | 0 | TPH | 0 | kg/h | 0
24 | RH RHS DESUP FLOW | TPH | 0 | kg/h | 0 | TPH | 2.99 | kg/h | 2990
25 | 1ST STAGE SHS DESUP FLOW | TPH | 0 | kg/h | 0 | TPH | 1.76 | kg/h | 1760
26 | 2ND STAGE SHS DESUP FLOW | TPH | 0 | kg/h | 0 | TPH | 0 | kg/h | 0
27 | SH SPRAY WATER PRESSURE | MPa (a) | 18.77 | bar (a) | 187.7 | MPa (g) | 18.77 | bar (a) | 188.713
28 | SH SPRAY WATER TEMP | °C | 175.8 | °C | 175.8 | °C | 169.99 | °C | 169.99
29 | RH SPRAY WATER PRESSURE | MPa (a) | 11.8 | bar (a) | 118 | MPa (g) | 11.8 | bar (a) | 119.013
30 | RH SPRAY WATER TEMP | °C | 160.9 | °C | 160.9 | °C | 160.9 | °C | 160.9
HPH
31 | HPH-6 FW I/L PRESSURE | MPa (a) | 18.98 | bar (a) | 189.8 | MPa (g) | 18.98 | bar (a) | 190.813
32 | HPH-6 FW I/L TEMP | °C | 175.8 | °C | 175.8 | °C | 177.49 | °C | 177.49
33 | HPH-6 FW O/L PRESSURE | MPa (a) | 19.03 | bar (a) | 190.3 | MPa (g) | 19.03 | bar (a) | 191.313
34 | HPH-6 FW O/L TEMP | °C | 205.5 | °C | 205.5 | °C | 206.35 | °C | 206.35
35 | HPH-6 EXT PRESSURE | MPa (a) | 1.744 | bar (a) | 17.44 | MPa (g) | 1.71 | bar (a) | 18.113
36 | HPH-6 EXT TEMP | °C | 472.38 | °C | 472.38 | °C | 472.38 | °C | 472.38
37 | HPH-6 DRIP TEMP | °C | 181.3 | °C | 181.3 | °C | 182.3 | °C | 182.3
38 | HPH-7 FW O/L PRESSURE | MPa (a) | 18.9 | bar (a) | 189 | MPa (g) | 18.9 | bar (a) | 190.013
39 | HPH-7 FW O/L TEMP | °C | 240 | °C | 240 | °C | 236.48 | °C | 236.48
40 | HPH-7 EXT PRESSURE | MPa (a) | 3.346 | bar (a) | 33.46 | MPa (g) | 3.29 | bar (a) | 33.913
41 | HPH-7 EXT TEMP | °C | 318.81 | °C | 318.81 | °C | 318.81 | °C | 318.81
42 | HPH-7 DRIP TEMP | °C | 211.1 | °C | 211.1 | °C | 211.22 | °C | 211.22
43 | HPH-8 FW O/L PRESSURE | MPa (a) | 18.8 | bar (a) | 188 | MPa (g) | 18.8 | bar (a) | 189.013
44 | HPH-8 FW O/L TEMP | °C | 274.5 | °C | 274.5 | °C | 273.85 | °C | 273.85
45 | HPH-8 EXT PRESSURE | MPa (a) | 5.755 | bar (a) | 57.55 | MPa (g) | 5.63 | bar (a) | 57.313
46 | HPH-8 EXT TEMP | °C | 387.92 | °C | 387.92 | °C | 387.92 | °C | 387.92
47 | HPH-8 DRIP TEMP | °C | 245.5 | °C | 245.5 | °C | 243.16 | °C | 243.16
48 | ECO I/L PRESS | MPa (a) | 18.49 | bar (a) | 184.9 | MPa (g) | 18.49 | bar (a) | 185.913
49 | ECO I/L TEMP-1 | °C | 274.5 | °C | 274.5 | °C | 274.92 | °C | 274.92
50 | ECO I/L TEMP-2 | °C | 274.5 | °C | 274.5 | °C | 272.59 | °C | 272.59
51 | DEA I/L COND PRESSURE | MPa (a) | 0.87 | bar (a) | 8.7 | MPa (g) | 0.87 | bar (a) | 9.713
52 | DEA I/L COND TEMP | °C | 138.7 | °C | 138.7 | °C | 139.54 | °C | 139.54
53 | DEA EXT STEAM PRESSURE | MPa (a) | 0.8348 | bar (a) | 8.348 | MPa (g) | 0.83 | bar (a) | 9.313
54 | DEA EXT STEAM TEMP | °C | 357.51 | °C | 357.51 | °C | 357.51 | °C | 357.51
55 | DEAERATOR PRESSURE | MPa (a) | 0.81 | bar (a) | 8.1 | MPa (g) | 0.81 | bar (a) | 9.113
56 | DEAERATOR TEMP | °C | 172.2 | °C | 172.2 | °C | 172.78 | °C | 172.78
57 | HW LEVEL | mm | 668.11 | mm | 668.11 | mm | 668.11 | mm | 668.11
58 | DEA LEVEL | mm | -39.54 | mm | -39.54 | mm | -39.54 | mm | -39.54
59 | #6 EXT STEAM FLOW RATE | TPH | 33.897 | kg/h | 33897 | TPH | 34.07 | kg/h | 34070
60 | #7 EXT STEAM FLOW RATE | TPH | 61.467 | kg/h | 61467 | TPH | 57.47 | kg/h | 57470
61 | #8 EXT STEAM FLOW RATE | TPH | 72.065 | kg/h | 72065 | TPH | 80.95 | kg/h | 80950
COOLING WATER SYSTEM
62 | COND I/L WATER TEMP- PASS A | °C | 34.37 | °C | 34.37 | °C | 34.37 | °C | 34.37
63 | COND O/L WATER TEMP- PASS A | °C | 43.61 | °C | 43.61 | °C | 43.61 | °C | 43.61
64 | COND I/L WATER TEMP- PASS B | °C | 34.02 | °C | 34.02 | °C | 34.02 | °C | 34.02
65 | COND O/L WATER TEMP- PASS B | °C | 43.91 | °C | 43.91 | °C | 43.91 | °C | 43.91
66 | COND I/L WATER PRESSURE- PASS A | bar(a) | 1.94 | bar (a) | 1.94 | bar (g) | 1.94 | bar (a) | 2.953
67 | COND O/L WATER PRESSURE- PASS A | bar(a) | 1.12 | bar (a) | 1.12 | bar (g) | 1.12 | bar (a) | 2.133
68 | COND I/L WATER PRESSURE- PASS B | bar(a) | 2.1 | bar (a) | 2.1 | bar (g) | 2.1 | bar (a) | 3.113
69 | COND O/L WATER PRESSURE- PASS B | bar(a) | 1.23 | bar (a) | 1.23 | bar (g) | 1.23 | bar (a) | 2.243
70 | CONDENSATE LHS WATER BOX DP | bar(a) | 0.9 | bar (a) | 0.9 | bar (g) | 0.9 | bar (a) | 1.913
71 | CONDENSATE RHS WATER BOX DP | bar(a) | 0.81 | bar (a) | 0.81 | bar (g) | 0.81 | bar (a) | 1.823
72 | LP EXHAUST HOOD (GOV) STEAM TEMP | °C | 48.79 | °C | 48.79 | °C | 48.79 | °C | 48.79
73 | LP EXHAUST HOOD (GEN) STEAM TEMP | °C | 47.66 | °C | 47.66 | °C | 47.66 | °C | 47.66
74 | CW-A CURRNT | Amps | 194.59 | Amps | 194.59 | Amps | 194.59 | Amps | 194.59
75 | CW-B CURRNT | Amps | 197.06 | Amps | 197.06 | Amps | 197.06 | Amps | 197.06
76 | CW-C CURRENT | Amps | -0.71 | Amps | -0.71 | Amps | -0.71 | Amps | -0.71
77 | CWP-A DISCH PRESS | bar(a) | 2.31 | bar (a) | 2.31 | bar (g) | 2.31 | bar (a) | 3.323
78 | CWP-B DISCH PRESS | bar(a) | 2.34 | bar (a) | 2.34 | bar (g) | 2.34 | bar (a) | 3.353
79 | CWP-C DISCH PRESS | bar(a) | 0.07 | bar (a) | 0.07 | bar (g) | 0.07 | bar (a) | 1.083
LPH
80 | CONDENSATE PRESS AFTER CV | bar(a) | 2.21 | bar (a) | 2.21 | bar (g) | 1.33 | bar (a) | 2.343
81 | LPH-1 I/L WATER TEMP | °C | 47.34 | °C | 47.34 | °C | 49.97 | °C | 49.97
82 | LPH-1 O/L WATER TEMP | °C | 59.1 | °C | 59.1 | °C | 55 | °C | 55
83 | LPH-2 O/L WATER TEMP | °C | 86.46 | °C | 86.46 | °C | 85.32 | °C | 85.32
84 | LPH-3 O/L WATER TEMP | °C | 107.6 | °C | 107.6 | °C | 107.16 | °C | 107.16
85 | LPH-4 O/L WATER TEMP | °C | 138.7 | °C | 138.7 | °C | 138.5 | °C | 138.5
86 | LPH-1 DRAIN TEMP | °C | 52.9 | °C | 52.9 | °C | 57.5 | °C | 57.5
87 | LPH-2 DARIN TEMP | °C | 64.65 | °C | 64.65 | °C | 70.98 | °C | 70.98
88 | LPH-3 DRAIN TEMP | °C | 92.02 | °C | 92.02 | °C | 94.17 | °C | 94.17
89 | LPH-4 DRAIN TEMP | °C | 113.1 | °C | 113.1 | °C | 120.7 | °C | 120.7
90 | EXT-4 STEAM PRESS. | bar(a) | 3.768 | bar (a) | 3.768 | bar(a) | 3.967 | bar (a) | 3.967
91 | EXT-4 STEAM TEMP | °C | 257.09 | °C | 257.09 | °C | 272.17 | °C | 272.17
92 | EXT-3 STEAM PRESS. | bar(a) | 1.449 | bar (a) | 1.449 | bar(a) | 1.525 | bar (a) | 1.525
93 | EXT-3 STAEM TEMP | °C | 156.459 | °C | 156.459 | °C | 194.96 | °C | 194.96
94 | LPH-2 I/L STEAM TEMP | °C | 89.9761 | °C | 89.9761 | °C | 125.44 | °C | 125.44
95 | LPH-2 I/L STEAM PRESS | bar(a) | 0.6811 | bar (a) | 0.6811 | bar(a) | 0.7139 | bar (a) | 0.7139
96 | LPH-1 I/L STEAM TEMP | °C | 61.87 | °C | 61.87 | °C | 66.61 | °C | 66.61
97 | LPH-1 I/L STEAM PRESS | bar(a) | 0.2172 | bar (a) | 0.2172 | bar(a) | 0.2277 | bar (a) | 0.2277
98 | IP EXHAUST PRESSURE | kPa (a) | 832.42 | kPa (a) | 832.42 | kPa (a) | 832.42 | kPa (a) | 832.42
99 | IP EXHAUST STEAM TEMP | °C | 357.5 | °C | 357.5 | °C | 357.5 | °C | 357.5
FEED WATER PUMPS
100 | BFP-A CURRENT | Amps | 387.66 | Amps | 387.66 | Amps | 387.66 | Amps | 387.66
101 | BFP-B CURRENT | Amps | 376.89 | Amps | 376.89 | Amps | 376.89 | Amps | 376.89
102 | BFP-C CURRENT | Amps | -1.72 | Amps | -1.72 | Amps | -1.72 | Amps | -1.72
103 | BFP-A I/L FW TEMP | °C | 173.51 | °C | 173.51 | °C | 173.51 | °C | 173.51
104 | BFP-B I/L FW TEMP | °C | 172.13 | °C | 172.13 | °C | 172.13 | °C | 172.13
105 | BFP-C I/L FW TEMP | °C | 72.19 | °C | 72.19 | °C | 72.19 | °C | 72.19
106 | BFP I/L FW TEMP | °C | 172.82 | °C | 172.82 | °C | 172.82 | °C | 172.82
107 | BFP-A FEEDWATER FLOW | TPH | 479.04 | kg/h | 479040 | TPH | 479.04 | kg/h | 479040
108 | BFP-B FEEDWATER FLOW | TPH | 472.06 | kg/h | 472060 | TPH | 472.06 | kg/h | 472060
109 | BFP-C FEEDWATER FLOW | TPH | 0 | kg/h | 0 | TPH | 0 | kg/h | 0
110 | BFP-A SUCTION PRESS | MPa (a) | 1.52 | bar (a) | 15.2 | MPa (a) | 1.52 | bar (a) | 15.2
111 | BFP-B SUCTION PRESS | MPa (a) | 1.51 | bar (a) | 15.1 | MPa (a) | 1.51 | bar (a) | 15.1
112 | BFP-C SUCTION PRESS | MPa (a) | 1 | bar (a) | 10 | MPa (a) | 1 | bar (a) | 10
113 | BFP-A SCOOP POSITION | % | 66.17 | % | 66.17 | % | 66.17 | % | 66.17
114 | BFP-B SCOOP POSITION | % | 74.94 | % | 74.94 | % | 74.94 | % | 74.94
115 | BFP-C SCOOP POSITION | % | 1.03 | % | 1.03 | % | 1.03 | % | 1.03
116 | BFP-A SPEED | RPM | 5099.92 | RPM | 5099.92 | RPM | 5099.92 | RPM | 5099.92
117 | BFP-B SPEED | RPM | 5442.48 | RPM | 5442.48 | RPM | 5442.48 | RPM | 5442.48
118 | BFP-C SPEED | RPM | 1.64 | RPM | 1.64 | RPM | 1.64 | RPM | 1.64
119 | BFP-A DISCHARGE PRESS | MPa (a) | 19.32 | bar (a) | 193.2 | MPa (g) | 19.32 | bar (a) | 194.213
120 | BFP-B DISCHARGE PRESS | MPa (a) | 19.33 | bar (a) | 193.3 | MPa (g) | 19.33 | bar (a) | 194.313
121 | BFP-C DISCHARGE PRESS | MPa (a) | 0.88 | bar (a) | 8.8 | MPa (g) | 0.88 | bar (a) | 9.813
122 | BFP-A DISCHARGE TEMP | °C | 175.79 | °C | 175.79 | °C | 175.79 | °C | 175.79
123 | BFP-B DISCHARGE TEMP | °C | 176.22 | °C | 176.22 | °C | 176.22 | °C | 176.22
124 | BFP-C DISCHARGE TEMP | °C | 43.48 | °C | 43.48 | °C | 43.48 | °C | 43.48
125 | TOTAL FEED WATER FLOW | TPH | 971.09 | kg/h | 971090 | TPH | 971.09 | kg/h | 971090
CONDENSATE EXTRACTION PUMPS
126 | CEP-A CURRENT | Amps | -0.29 | Amps | -0.29 | Amps | -0.29 | Amps | -0.29
127 | CEP-B CURRENT | Amps | 58.83 | Amps | 58.83 | Amps | 58.83 | Amps | 58.83
128 | CEP I/L TEMP | °C | 45.93 | °C | 45.93 | °C | 47.25 | °C | 47.25
129 | CEP I/L PRESSURE | kPa (a) | -0.07 | kPa (a) | -0.07 | kPa (g) | -0.07 | kPa (a) | -0.05987
130 | CEP-A DISCHARGE PRESS | MPa (a) | -0.02 | bar (a) | -0.2 | MPa (g) | -0.02 | bar (a) | 0.813
131 | CEP-B DISCHARGE PRESS | MPa (a) | 1.66 | bar (a) | 16.6 | MPa (g) | 1.66 | bar (a) | 17.613
132 | CEP O/L TEMP (GSC I/L) | °C | 45.93 | °C | 45.93 | °C | 47.96 | °C | 47.96
133 | CEP O/L PRESSURE | MPa (a) | 1.64 | bar (a) | 16.4 | MPa (g) | 1.64 | bar (a) | 17.413
134 | CEP CONDENSATE FLOW | TPH | 738.47 | kg/h | 738470 | TPH | 738.47 | kg/h | 738470
135 | CEP RECIRCULATION FLOW | TPH | 6.41 | kg/h | 6410 | TPH | 6.41 | kg/h | 6410
136 | CCW-A CURRENT | Amps | 21.84 | Amps | 21.84 | Amps | 21.84 | Amps | 21.84
137 | CCW-B CURRENT | Amps | 21.81 | Amps | 21.81 | Amps | 21.81 | Amps | 21.81
138 | CCW-C CURRENT | Amps | -0.06 | Amps | -0.06 | Amps | -0.06 | Amps | -0.06
139 | VACUUM PUMP-A CURRENT | Amps | 162.93 | Amps | 162.93 | Amps | 162.93 | Amps | 162.93
140 | VACUUM PUMP-B CURRENT | Amps | 158.35 | Amps | 158.35 | Amps | 158.35 | Amps | 158.35
141 | COND FLOW-1 | TPH | 730.72 | kg/h | 730720 | TPH | 730.72 | kg/h | 730720
142 | COND FLOW-2 | TPH | 733.1 | kg/h | 733100 | TPH | 733.1 | kg/h | 733100
143 | HRH PRESS AT IP I/L | MPa (a) | 3.08 | bar (a) | 30.8 | MPa (g) | 3.08 | bar (a) | 31.813
144 | FIRST STAGE STM TEMP | °C | 480.14 | °C | 480.14 | °C | 480.14 | °C | 480.14
145 | FIRST STAGE METAL TEMP | °C | 469.75 | °C | 469.75 | °C | 469.75 | °C | 469.75
146 | GV1 POS | % | 24.74 | % | 24.74 | % | 24.74 | % | 24.74
147 | GV2 POS | % | -0.76 | % | -0.76 | % | -0.76 | % | -0.76
148 | GV3 POS | % | 100.92 | % | 100.92 | % | 100.92 | % | 100.92
149 | GV4 POS | % | 100.96 | % | 100.96 | % | 100.96 | % | 100.96
150 | AUX GLAND STM PCV POS | % | -0.26 | % | -0.26 | % | -0.26 | % | -0.26
151 | GLAND STM OVERFLOW VALVE POS | % | 87.75 | % | 87.75 | % | 87.75 | % | 87.75
152 | GLAND STM SPRAY VALVE POS | % | 32.53 | % | 32.53 | % | 32.53 | % | 32.53
153 | D/A CONTROL STATION VALVE OPENING | % | 100.17 | % | 100.17 | % | 100.17 | % | 100.17
UU-ACCOUNTED LOSSESS
154 | Test duration | hours | 4 | hours | 4 | hours | 4 | hours | 4
155 | Hotwell storage change | TPH | 0 | kg/h | 0 | TPH | -1.6636 | kg/h | -1663.582
156 | Deaerator storage change | TPH | 0 | kg/h | 0 | TPH | 0 | kg/h | 0
157 | Inadvertant make-up | TPH | 0 | kg/h | 0 | TPH | 0 | kg/h | 0
158 | Unaccounted-loss | TPH | 0 | kg/h | 0 | TPH | 0 | kg/h | 0
159 | Feedwater pump outboard leakage | TPH | 0 | kg/h | 0 | TPH | 0 | kg/h | 0
CT FANS
160 | CT FAN-1 CURRENT | Amps | 126.63 | Amps | 126.63 | Amps | 126.63 | Amps | 126.63
161 | CT FAN-2 CURRENT | Amps | 130.33 | Amps | 130.33 | Amps | 130.33 | Amps | 130.33
162 | CT FAN-3 CURRENT | Amps | 114.36 | Amps | 114.36 | Amps | 114.36 | Amps | 114.36
163 | CT FAN-4 CURRENT | Amps | 113.12 | Amps | 113.12 | Amps | 113.12 | Amps | 113.12
164 | CT FAN-5 CURRENT | Amps | 112.72 | Amps | 112.72 | Amps | 112.72 | Amps | 112.72
165 | CT FAN-6 CURRENT | Amps | 122.27 | Amps | 122.27 | Amps | 122.27 | Amps | 122.27
166 | CT FAN-7 CURRENT | Amps | 124.17 | Amps | 124.17 | Amps | 124.17 | Amps | 124.17
167 | CT FAN-8 CURRENT | Amps | 120.66 | Amps | 120.66 | Amps | 120.66 | Amps | 120.66
168 | CT FAN-9 CURRENT | Amps | 119.13 | Amps | 119.13 | Amps | 119.13 | Amps | 119.13
169 | CT FAN-10 CURRENT | Amps | 143.81 | Amps | 143.81 | Amps | 143.81 | Amps | 143.81
170 | CT FAN-11 CURRENT | Amps | 118 | Amps | 118 | Amps | 118 | Amps | 118
171 | CT FAN-12 CURRENT | Amps | 81.8 | Amps | 81.8 | Amps | 81.8 | Amps | 81.8
172 | LP EXHAUST DRYNESS FRACTION | % | 93.5171 | % | 93.5171 | % | 93.5171 | % | 93.5171
173 | Aging month/s, after overhaul | months | - | months | - | months | 9 | months | 9
174 | Aging Factor | % | - | % | - | % | 0.82 | % | 0.82
175 | RH Pressure drop | % | 10 | % | 10
| Make up water | TPH | 0 | TPH | 0 | 0 | TPH | 0 | TPH